## Slide 1: SCADA IN INDIAN POWER SYSTEM
By Tapobrata Paul
Dy Manager (System Logistics)
NERLDC, POSOCO

## Slide 2: POWER SYSTEM COMPONENTS
Power Plant
Generation
Residential
Customer
Commercial/
Industrial
Customer
Residential
Customer
Distribution
Pole
Urban
Customers
Primary Distribution
66 kV
Transmission
Distribution Transformer
(11/0.415 kV)
Secondary Grid
(66/11 kV)
Primary Grid
(220/66 kV)
Secondary Distribution
Underground Cable
To Other
66Kv
Substations
Primary Transmission(132/220/400/765KV)
Secondary Transmission(66/132KV)
CB
X’mer
(11/220kV)
Sending end SS
Bus-bar
Bus-bar
Steel Tower
CB
NTPC/NHPC etc.
POWERGRID
STU
FACTORY
NERLDC

## Slide 3: HIERARCHICAL CONTROL CENTRE SETUP
NLDC
NRLDC
SLDC
RTU
5 Nos. RLDC
07 Nos. SLDC
RTU
RTU
SLDC
SLDC
ERLDC
NERLDC
SRLDC
WRLDC
CS GEN.
Stn.
POWERGRID
Sub Stn.
RTU
RTU
NERLDC
Data Collection Units

## Slide 4
ARUNACHAL PRADESH
ASSAM
MEGHALAYA
MANIPUR
NAGALAND
MIZORAM
TRIPURA
UTILITIES CONTROLLED UNDER NERLDC
SEVEN STATES THROUGH RESPECTIVE SLDCs
CENTRAL SECTOR GENARATING STATIONs
Examples:
NEEPCO
NHPC
NTPC
TRANSMISSION UTILITIES
Example:
POWERGRID (Through RTAMC)
Examples:
AS,ME,TE,MI,MA,NA,AR
NERLDC

## Slide 5: WHAT IS SCADA?
SUPERVISORY CONTROL AND DATA ACQUSITION
NERLDC
ASPECTS:
Supervision – Monitoring.
Control – Supervisory.
Data Acquisition System :
a system provided to record the sequence of operation in time, of the relays/equipment as well as the measurement of pre-selected system parameters.

## Slide 6: WHY SCADA?
AUTOMATION Requirements
  Managing Hazardous/Complex/ Sequential /Repetitive Operations
  Centralized management requires feedback
Faster response : quicker and informed decision making
Faster restoration after breakdown
Optimisation of resources, Reduction of losses, and lower operational cost
Increased security, availability, reliability, and efficiency
POWER SYSTEM NEEDS
Before SCADA : Less and delayed information.
  Real time disturbance handling problems.
NERLDC

## Slide 7
DATA ACQUISITION SYSTEM:
Data flow direction:
SLDC
RLDC
SLDC
Sub-LDC
Central Sector
RTUs
RTU
Wide Band /
PLCC Commn
Wide Band
Commn
Wide Band
Commn
(FO)
RTU
Wide Band
Commn
NLDC
RTU
Substation Level

## Slide 8: BLOCK DIAGRAM OF A TYPICAL SCADA SYSTEM
SCADA
H/W &
S/W
MEDIA
C
O
M E
M Q
P
T
C
O
M E
M Q
P
T
Remote
Terminal
Unit
T P
R A
A N
N E
S L
D
U
C
E
R
C & R
PANEL
CONTROL
CENTRE
SUBSTATION / GENERATNG
STATION
COMMUNICATION
MEDIA
NERLDC

## Slide 9
NERLDC
SUBSTATION LEVEL

## Slide 10
CURRENT TRANSFORMER
POTENTIAL TRANSFORMER

## Slide 11: SCADA HARDWARE CONNECTIVITY WITH COMMUNICATION SYSTEM AT SUB-STN/GEN ST
RTU
N
S
K
5
PLCC T x / R x
SPEECH / DATA
PANEL
RS 232 CONNECTIVITY
PLCC
INDOOR EQUIMENT
TO POWERLINE
NERLDC

## Slide 12
RTU
EPBAX
COMMUNICATION SYSTEM (CONT.)
NERLDC

## Slide 13
WAVE TRAP
CAPACITOR VOLTAGE TRANSFORMER
NERLDC

## Slide 14: SCADA HARDWARE CONNECTIVITY WITH COMMUNICATION SYSTEM (WIDE BAND)
RTU
MUX
RADIO
TX / RX
OLTE
OLTE
RADIO
TX / RX
MUX
MUX
MUX
FEP
FEP
RTU
DIGITAL MICROWAVE
FIBER OPTIC SYSTEM
SUBSTATION/ GEN STN SIDE
CONTROL CENTRE
OPGW
NERLDC

## Slide 15: <photos of RTU> <photos of PLCC Panel> <photos of communication panels>
RTU PANEL
RTU
PLCC PANEL

## Slide 16: DATA FLOW COMMUNICATION PROTOCOL
RTU
RLDC
FEP
SLDC ICCP
SERVER
RLDC ICCP SERVER
BROADCASTS IN
SLDC LAN
PLCC/BROADBAND
ICCP
ICCP
BROADCASTS IN
RLDC LAN
RTU
RTU
SLDC/ Sub LDC
FEP
NLDC
IEC 60870-5-101/104
NERLDC

## Slide 17: SCADA ARCHITECTURE
WORK STATION
SCADA/EMS
EXTERNAL DMZ
CFE
GPS
VPS MODULE
ISR
RTUs IEC 60870-5-104
NMS
ICCP
RD SERVER
SCADA LAN
DTS LAN
PDS SERVER
DATA ACQUISITION LAN
WORK STATION
SLDC/ OTHER UTILITIES/ OTHER RLDC
ALL PRINTERS
EXTERNAL FIREWALL
WEB SERVER/Patch management server
INTERNAL FIREWALL
DTS SERVER
OFFICE NETWORK
DATA LAN
ICCP LAN
INTERNAL DMZ
PDS LAN
OFFLINE LAN
WORK STATION
F/W ROUTER
F/W ROUTER
RTUs IEC 60870-5-101

## Slide 18: SCADA Basic Functions
Data Acquisition:
Process of acquiring data from monitored system.
We use eterrascada.
To acquire data in the monitored system, the e‑terrascada Front End performs the following functions:
* Scans the monitored system at prescribed times and receives data from RTUs via the CFEs.
* Performs conversion and checking on raw data to make it usable for display to operators and other applications.
* Determines the quality of data and marks data that may not be reliable.
* Allows e‑terrascada operators to request scanning of individual scan groups.
e‑terrascada can acquire, process, and display data from three types of devices in the monitored system. These device types are:
* Variable-state devices, which have numerical measurements, referred to in e‑terrascada as “analog points”
* Discrete-state devices, such as circuit breakers and isolators, which have status measurements, referred to as “status points “.
NERLDC

## Slide 19: SCADA Basic Functions
Data Processing :
  Data quality flags : GOOD, SUSPECT, REPLACED, ESTIMATED, NIS
  Alarm checking :
    Status :
      Illegal and abnormal state
      Alarming transitions
    Analogs :
      Limits checking
      Calculation triggering
  Topology processing
Power System Analysis
  Contigency analysis
  Real time network analysis
  State Estimation
  Sequence of events
NERLDC

## Slide 20: Supervisory Controls
Supervisory controls are provided for :
  Switching device (open/close)
SCADA Basic Functions
NERLDC

## Slide 21: Supervisory Control Checks
The console issuing the control must have appropriate permission
The controlled point Quality Flag must be GOOD
  If suspect, the operator may not see the feed back of the control but the control is authorized.
If the point is already in the commanded state, a warning message appears.
If the control asked is prevented by a tag, the control is rejected.
Interlocks must be satisfied
The associated RTU must be in service
The controlled point must not already be Selected or have a control pending
NERLDC

## Slide 22: SCADA EMS
By Tapobrata Paul
Engineer (System Logistics)
NERLDC, POSOCO

## Slide 23: Introduction
Power System Overview
Definition of SCADA & EMS
More Details
NERLDC

## Slide 24: Topics
 Modeling Power System Components
 State Estimator, Real Time Network (RTNET)
 Contingency Analysis
 Load Forecast
 Optimal Power Flow, Security Enhancement (SENH),
Voltage VAr Dispatch (VVD)
NERLDC

## Slide 25: Modelling Power System Components
NERLDC

## Slide 26: Modelling Power System Components
Network Model Assumptions
Network Database and Structure
Modeling Connectivity and Substation Structure
Load and Load Area Model
Network Component Model and their Parameters
Network Schedules
Generation Model
Validation
NERLDC

## Slide 27
 Basic network model assumptions
3 phase balanced system
  implies transposed lines
  allows network modeling by a single phase equivalent
branch equivalent PI model
shunt conductance neglected (corona effect negligible)
mutual admittances are neglected (except in SCT)
Resistances defined at nominal temperature
reactances defined at nominal frequency
 Special assumptions for unbalanced short circuit calculations
negative sequence impedances equal to positive sequence impedances
no need to model ground return paths explicitly
NERLDC
Network Model Assumptions

## Slide 28: Sign conventions for Flows
R + j X
BCH
2
BCH
2
Generators
( inductive )
Stepups
Line compensation
Line equivalent PI
Shunt reactance
( inductive )
( reactor )
Shunt reactance
( capacitive ) ( capacitor )
Load
( through
stepdowns )
MW sign conventions : Generators : positive to bus
Branches and loads : positive from bus
Busbar (node / bus)
MVAr sign conventions :
Generators and shunts : positive to bus Branches and loads : positive from bus
NERLDC

## Slide 29: NETMOM is the core database for Network Model
Validates
the
network model
Using applications (each with its own copy of NETMOM) :
NETMODEL
RTNET :
Real-Time NETwork
CA :
Contingency Analysis
Topology of power network
. Description of network components
positive sequence
zero sequence
. Equivalent models
. Load and CB forecast schedules
. Regulation schedules
. Load models
. Operating limits
. Application specific data
Network Database
NETMOM
SCT :
Short-CircuiT
PWRFLOW :
Power FLOW solution
SENH :
Security ENHancement
OPF :
Optimal Power Fl
NERLDC

## Slide 30
Partial Structure of NETMOM Database
Company Division
Substation Voltage level
(component group)
Unit (generator) Station auxiliary load Demand load
Shunt (capacitor or reactor) DC converter
Node
Switching device type
Switching device
Transformer (physical device) Transformer (winding pair)
Phase-shifting tap
Transmission line
Two terminal line segment Zero impedance branch DC line
Load type Load-area
Forecast schedules (by type) Operating area
Equivalent impedances
DECK CO
DV
DCLN
LDTY LDAREA
SKEDTY AREA EQUIV
LINE
LN ZBR
ST
XFMR
CBTYP
KV
UN
AUX LD
CP DCCNV
ND
CB
XF
PS
NERLDC

## Slide 31: Modeling connectivity elements
 Nodes and switching devices
Node = set of rigidly connected
links and bus-bars
“green” node
“red” node
“blue” node
“yellow” node
NERLDC

## Slide 32: Substation structure
BUS = set of nodes connected by closed switches
: external node
“Red” bus
NERLDC

## Slide 33: Bus Load Model
 Specifies where, when, and how much power is extracted from the network
 Distributes system MW load onto bus loads
baseload + fraction of (system load)
Bus load =
“fraction”
parameters (distribution factors) are updated by an
adaptive algorithm using “observation points” provided by each run of the state estimator
 A more complex hierarchical model of bus loads can be
setup. For example :
System load
  Geographical area load (East, West, ...)
(residential, industrial, commercial, ...)
Sectoral subdivision
  Bus loads
PL + j QL
NERLDC

## Slide 34: Example of a load tree
Top level load area ( forecast area )
Load area A WEST
Load a
Load area B EAST
Load area B1 RESIDENTIAL |  |  | Load area B2 COMMERCIAL | 
Load b
Load c
Load d
Load e
Load f
NERLDC

## Slide 35: Load distribution mechanism in a load tree
Top level load area
Load area A
Load a
Load area B
Load area C
Load b
Load c
Load d
Base : 100
Fraction : 200
Base : 1000
Fraction : 0.88
Base : 80
Fraction : 100
Base : 200
Fraction : 300
Base : 0
Fraction : 50
Base : 0
Fraction : 100
Base : 60
Fraction : 300
Base : 10
Fraction : 0
280 + 600 = 880
80 + 150 = 230
200 + 450 = 650
110 + 540 = 650
100 + 540 = 640
10 + 0 = 10
0 + 230 = 230
60 + 580 = 640
0 + 145 = 145
60 + 435 = 495
NERLDC

## Slide 36: Example of load tree structure
Top level load area
( forecast area )
Load-area
Bo (all fixed bases)
Load- area I1 INDUS
1 shift
Load-area R RESIDENTI AL
Load-area C COMMERCIA L
a
Load-area
B
(all time dependentb ses)
Load-area
B1
(all time
dependentba
ses)
Load- area I3 INDUS
3 shifts
Load- area I2 INDUS
2 shifts
NOT proportional to total load ;
NOT updated by SE
Proportional to total load and
tracked by SE
NERLDC

## Slide 37: Time dependence of loads
 Week
subdivision into
WEEK SEGM ENTS
From | SUN | 00:00 | to | MON | 12:00 | Day seg : WE
From | MON | 12:00 | to | FRI | 12:00 | Day seg : WRK
From | FRI | 12:00 | to | FRI | 24:00 | Day seg : FRI
From | SAT | 00:00 | to | SAT | 24:00 | Day seg : WE
 Day
subdivision into a set of DAY SEGMENTS
WE day segments :
  00:00 - 08:00 - 09:00 - 11:00 - 17:00 - 19:00 - 23:00
 A set of day segments is assigned to each week segment
 Day segments repeat themselves within the same week segment
 Load characteristics are constant within a day segment
NERLDC

## Slide 38: Entering data for loads (summary)
Enter data for individual loads :
Load area
Base MW load value
Parent MW fraction
Base MVAr load value
Load MVAr schedule name
NERLDC

## Slide 39: Modeling generating units
 Insert UN records
 Enter unit parameters :
rated MVA
regulation schedule name
base MW
min, max MW
participation factor
ramp rate
corresponding GENMOM unit
 Define unit regulation schedules and enter schedule values
 Define MVAr capability curve table
PG + j QG
NERLDC

## Slide 40: GENERATOR FEASIBLE OPERATING DOMAIN (MVAr capability "curve")
MVAr limits
MW
output
Several such curves can be stored
User selects the desired curve
 Reflects :
Max MVAR Capability
MVA limit due to the stator current
prime mover MW capability
NERLDC

## Slide 41: Modeling shunt capacitors
Capacitor
Reactor
 1. Insert CP records
 2. Enter shunt capacitor nominal MVAr (negative value indicates a “reactor”)
 3. Enter name of node where
voltage is regulated
(must have a CB to regulate)
 4. Enter a regulation schedule
NERLDC

## Slide 42: Modeling Lines
 Insert Line records
records
Insert line segments records
  LN
  LNLIM
Insert zero impedance branch
  ZBR
  ZBRLIM
Resistance | R % |  | (on a 100 MVA / nominal voltage base)
Reactance | X % |  | (on a 100 MVA / nominal voltage base)
Line Charging | BCH | % | (on a 100 MVA / nominal voltage base)
 Enter line segment parameters :
 Percent value = 100 * perunit value
 Perunit value = ohm value / impedance base
 Impedance base = square of voltage base / power base
 Enter line length
NERLDC

## Slide 43: Line parameters
PI model for a line segment
“FROM” Bus k
“TO” Bus m
0.5 BCHk
m
0.5 BCHk
m
Rkm + j Xk
m
Resistance | R % |  | (on a 100 MVA / nominal voltage base)
Reactance | X % |  | (on a 100 MVA / nominal voltage base)
Line Charging | BCH | % | (on a 100 MVA / nominal voltage base)
NERLDC

## Slide 44: Modeling transformers
 Insert XFMR, XF records
 Define transformer tap types :
tap type name
min, max, nominal tap position
per unit step size
time delay before tap can move
 Define transformer regulation schedules
 Enter transformer parameters :
nameplate information
tap type for each side
normal tap position for each side
voltage sensitivity
master / follower and current balancing flag
PI model and saturation coefficients (see next slide)
“FROM”
LTC side “I” side
“TO”
FIXED side “Z” side
NERLDC

## Slide 45: Transformer model : impedances
 Transformer model :
R + j X
U1
kU2
Gmag
(iron
loss)
Bmag
(magnet. suscept.)
I1
R and X parameters can be determined by short-circuit test
Gmag and Bmag
parameters can be determined by open-circuit test
NERLDC

## Slide 46: Defining Transformer Tap Types
min tap
nominal tap (causes no change in voltage)
per unit step size
 For a voltage transformer, the tap model refers
to voltage magnitude
 Tap type :
max tap
Per unit step size for a transformer =
per unit increase in voltage transformation k = ( V1 / V2 )
that occurs with each increase of the tap position.
Step size is positive if k (MaxTap) > k (MinTap), negative otherwise
Example :
Step size = + 0.005
MaxTap = +16 ===> V1/V2
= 1.08
===> V1/V2
Nominal = 0
= 1.00
===>
MinTap = -16
V1/V2 = 0.92
NERLDC

## Slide 47: Effect of tap position in Modelling
NERLDC

## Slide 48: GE NERATION data base :
 Hierarchy defines the existence of generation
system components :
Operating areas ( OPA )
Plant controllers ( PLC )
  Generating units ( UNIT )
Utilities ( UTIL )
  Tie corridors ( TIE )
    Tie lines ( TYLN )
Transacting areas ( TRA )
 Fuel types
 Generation types
 Allowable transaction types and actual transaction data are stored in a separate database (TSKED)
FUELTY
GENMOM
OPA
GENDECK
UTIL
TIE
TYLN
PL
PLC
UNIT
TRA
GTYPE
NERLDC

## Slide 49: GENERATION CONTROL
 Basic concepts
Operating area (OPA)
(also called "control area")
Portion of the electric power system in which generation is centrally controlled to ensure continuous matching between supply and demand
Isolated operating area
Frequency variation speed is a measure of the current imbalance between generation and load
Frequency is an integrated measure of the generation and load imbalance
Interconnected operating areas
Interchange flows have to be controlled to the scheduled value by each OPA
Load
Gen
Load
Gen
Load
Gen
Loads
Generators
NERLDC

## Slide 50: Generation control organization
Control center ( EMS)
*
Power station
PLC
Unit
Operating constraints
Cost elements
Current status / generations / frequency
Controls
Local frequency regulation (speed governor)
( Base-points schedules )
AGC (RTGEN)
Control centers
of other control areas
Interchange transactions
NERLDC

## Slide 51: State Estimator: Real Time Network (RTNET)
NERLDC

## Slide 52: Network Validation
Information (Information to the user not Harm-ful)
Warnings (to so that the model can be improved)
Hanging Nodes etc.
All Warnings need not be harmful.
Errors (Harmful)
All errors should be removed before the model can be set
online.
NERLDC

## Slide 53: Real Time Network (RTNET)
Topics
 RTNET functions
 State estimator variables and equations
 Weighted least squares (WLS)
 Measurement weights - accuracy classes
 Observability
 Pseudo-measurements
 Estimation procedures
NERLDC

## Slide 54: RTNET (CONT.)
functions
 Determine the network state given :
the network model (equations and parameters)
the network topology (derived from status measurements)
available analog measurements
models of load and generation bus injections
 Inform about possible violations of operating constraints
 Identify anomalous measurements
 Calculate measurement error statistics
 Identify modeling errors
 Improve modeled information
 Calculate loss sensitivities
NERLDC

## Slide 55: State Estimator variables
 State vector X
State variables [X] consist of a subset of the variables characterizing the electrical state of the power system. They are explicitly solved by the state estimation algorithm. Basically, X = complex voltage vector.
The remainder of the power system variables are deterministically
dependent on the state variables:
Y =h(X)
Basically, Y = complex power flows.
 Measurement vector Y
Bus voltage magnitudes
MW and MVAr flows in lines, transformers, and bus injections
Transformer tap positions
 Other variables or parameters in R T N E T not related to the current
electrical state of the system :
Measurement bias and standard deviation
NERLDC

## Slide 56: State Estimator Equations :
 Bus balance equations (First Kirchhoff law):
Require the sums of real power flows and reactive power flows into a bus to be zero.
Zero injection bus equations are associated with relatively high levels of confidence (low uncertainty).
 Measurement equations relate a measurement to :
either directly a solution variable (voltage magnitude)
or an implicit value calculated from solution variables (power flows)
NERLDC

## Slide 57: Least Squares State Estimation
lThe
measurement equations are :
where
Y = h(X) + V
X = column-vector of state variables
Y = column-vector of measurements
V = column-vector of measurement errors (zero mean, uncorrelated, Gaussian)
l This is an over-determined powerflow problem
using the information from M independent measurements
Y = { yj }
to solve for N unknowns (state X or solution variables), where
M is greater than N ( M-N = degree of freedom )
NERLDC

## Slide 58: Weighted Least Squares (WLS )
 The best estimate of the state variables X is obtained by the Weighted Least Squares (WLS) method. The objective is to minimize the sum of the squares of the weighted deviations of the estimated measurements from the actual measurements:
Min J(X) = Sumj { [ yj - hj(X) ] / σj }2
σ reflects the measurement uncertainty
The value of J is called the “cost” of the solution.
 In matrix notation,
J(X) = [y-h(X)]T W-1 [y-h(X)]
W is the covariance matrix of measurement errors, which reflects the measurement confidence. In the case of independent measurement errors, W-1 is diagonal with
j
wjj = 1/σ 2
NERLDC

## Slide 59: WLS iteration types
Xk+1 - Xk
= [ HT W-1 H ]-1 HT W-1 [ Y-h(Xk) ]
 FACTOR :
Full rebuild of all matrices and factorization of the normal matrix with optimal reordering ( in case of topology change or change in the set of available measurements )
 REFACTOR :
Same without revising the factorization order
 REPEAT :
Recalculate only the RHS and use the same normal matrix inverse to update X
 RHS :
Repeat with updated W for de/re-weightings
NERLDC

## Slide 60: RTNET State Estimator solution convergence cycles
Solve linearized WLS problem
Voltage converged
?
Solution valid
?
Implement weight changes
Get measurements from SCADA Filter gross errors
Update measurement error statistics
NERLDC

## Slide 61: Estimating injection components
 Branch flow estimates yield net injection estimate
NIest = 38 + 53 = 91
 Measured net injection = 100 – 12 = 88
 Measurement error = 91 – 88 = +3  injection component estimates must be further apart than measured values
 Allocate correction to injection component in proportion of their variances :
Gest = Gmeas + 3 * (0.3 / 0.3 + 1) = 100 + 0.69 = 100.69
Dest = Dmeas - 3 * (1 / 0.3 + 1) = 12 – 2.31 = 9.69
 In this process, pseudo-measurements and their variances are used in case of
lacking measurement(s)
Gmeas=100 ; sigma2=0.3
Est =53
meas
D =12 ; sigma2=1
Est =38
NERLDC

## Slide 62: RTNET
Observability
 Measurement-Observable (or strictly speaking : “observable”) Portions of the network where RTNET can estimate the state using only actual measurements.
 Observable (or strictly speaking : “solvable”)
Portions of the network where RTNET can calculate the state using available measurements, complemented by pseudo-measurements (based on modeled information).
= set of “non-measurement observable” buses
MW MVAr
kV



MW MVAr
MW MVAr
MW
MVAr


TAP
MW MVAr
S
S
NERLDC

## Slide 63: RTNET : unified solution for observable and unobservable
 Pseudo-measurements are used to complement actual measurements in order to allow full network solution
 Pseudo-measurements are generated from :
MW generation from economic dispatch / commitment
MVAr generation from voltage regulation schedules
MW / MVAr load models and schedules (updated from past records)
 Above information translates into a single type of pseudo- measurement: unit and load injections
 Measurement vector Y is extended to include minimal number of pseudo-measurements
 Pseudo-measurements are given greater uncertainty than actual measurements
NERLDC

## Slide 64: RTNET: Summary
STATE ESTIMATOR
Solve the normal WLS equations (derived from the m measurement eq. ) for the actual network
under current conditions
Estimate of :
voltage angles 
voltage magnitudes V
Branch flow equations
Estimate of :
Branch flows
Injections
Measured values of :
Topology (switch pos.)
Voltages Injections (G-L) Branch flows
Tap pos.
 Measurements you define have more influence on the result than other measurements
 Uses the WLS approach to find a network state that is most consistent with:
all the measured data
the modeled data (pseudo-measurements)
 Estimates tap positions
 Unified solution for measured and non-measured portions of the network
NERLDC

## Slide 65: RTNET: Inputs and Outputs
Output :
Bus voltages and angles
MW / MVAr flows
Limit violations
Generations and loads
LTC tap positions
Anomalous input data
Loss sensitivities
RTGEN
Unit MW base-points and MW limits
Unit participation factors
Unit ramp rates
Unit control status and on/off-line status
Scheduled area transactions
•
Network component MW and MVAr flow measurements
Bus voltage mag. & angle meas.
Transformer and phase shifter tap positions
Data quality information
SCADA
RTNET
NETMOM
G G
NETMODEL
NETMOM
G
G
NERLDC

## Slide 66: RTNET’s checks on input data
 SCADA performs a quality check before passing data to RTNET
 RTNET uses SCADA’s quality evaluation to determine whether or not to use the data
 RTNET performs elementary coherency checks to ignore measurements in gross error :
voltage on de-energized nodes
flows across open switches
Flows exceeding a multiple of the branch limit
MW or MVAr generator flows exceeding the MVA rating of the unit
MW or MVAr loads exceeding the load limits
Measurements outside reasonability limits
NERLDC

## Slide 67: RTNET : Results
Monitoring
RTNET
NERLDC

## Slide 68
the network state
Network substation diagram
SCADA substation diagram
RTNET : Results
NERLDC

## Slide 69
Network oneline diagram
NERLDC

## Slide 70
Bus Symbolic View of the Bus Summary display
NERLDC

## Slide 71: State estimation: ASSUMPTIONS
Basic network model assumptions
3-phase balanced system
mutual admittances are negligible (except in SCT)
branch equivalent PI model
shunt conductances neglected (corona effect negligible )
impedances defined at nominal frequency
Specific assumptions for the state estimator : correct impedances
correct topology
correct line parameters R, X, BCH
correct transformer models:
  Losses (iron, copper)
  Magnetization susceptance
  Tap: position, model (sign, step, impedance effect)
 Special assumptions for measurements:
correct measurement location (point-to-point tests)
no bias
correct weight ( = correct measurement error variance)
NERLDC

## Slide 72: RTNET : Error detection
 Error detection
Based on CHI-square test:
  the solution cost “J” follows a CHI-square distribution with M-N degrees of freedom
( M-N = number of measurements – number of state variables).
  J will be larger than expected in the presence of bad measurement data
 Error identification
Based on equation residuals evaluated at the calculated network state:
  Residual = estimated value - measured value
  Large residuals generally indicate that the associated measurement (or bus equation) is grossly in error or anomalous
NERLDC

## Slide 73: Contingency Analysis
NERLDC

## Slide 74: Contingency Analysis : Overview
kV
 Contingency Analysis reports which hypothetical contingencies would cause operating limit violations
 Flexible contingency definition
 Contingency groups
What if this generator
is outaged ?
What if this transformer is outaged ?
NERLDC

## Slide 75: Contingency Analysis
Contingency analysis covers a variety of analytical investigations performed by both system planners and operators.
The system planner’s objective is to identify the network elements that will be required to maintain system operation within planning criteria.
The general requirement is to identify capital investments and operating costs for long term future developments.
The system operator’s objective is to identify the manner in which the system must be operated to maintain system security both in the near term (days, weeks, months) with existing network elements or the medium term (one to three years) during which a limited amount of equipment could be installed.
NERLDC

## Slide 76: Reliability Testing Criteria for Contingency Analysis (Steady State)
Single contingencies (N-1). Loss of any transmission line or transformer or generator. These are often termed probable or credible contingencies.
Double contingencies (N-2). Simultaneous loss of two single-circuit transmission lines, a double-circuit line or dc bipole. Variations on these contingencies exist worldwide specifically with respect to the definition of double circuit and the option of non-simultaneity of loss (N-1-1). These too are credible or probable contingencies.
Less probable contingences and/or extreme contingencies can include loss of entire substations or multiple generators.
Conditional Contingencies
NERLDC

## Slide 77: RTCA : Features
Flexible contingency definition :
defined by selecting components in a software prepared list
any combination of component outages and breaker
switching is allowed
any bus structure allowed
Very fast solution :
Contingency screening
Well-developed power flow algorithms for :
  ultra-fast approximate solution ( for contingency screening
)
  full accurate power flow solution for definite assessment
Accurate modeling of the power system behavior:
Conditional contingencies for simple relay modeling
Automatic controller response modeling
NERLDC

## Slide 78: RTCA processing : Screening, selection and full solution
INITIALIZATION
Solve basecase network
SCREENING
Calculate fast approximate solution for each contingency
( local or widespread )
C C
C C
C
1
2
3
4
5
Retained contingencies
Potentially harmful contingencies
( contingencies that have screening violations)
C
C
C
1
2
3
Active contingencies
SELECTION
Rank potentially harmful contingencies
based on
Select highest ranked contingencies screening violation severity
FULL solution
Solve selected contingent networks
C
C C
C
C
C
C
C
C
C C
C
C
C
C
C C
C
C
C
C
C
C
C
C
C
C C C
NERLDC

## Slide 79: Contingency: Types
Primary contingency (standard)
Conditional:
specify a component (node or branch)
Specify the condition:
  Node voltage > or < some threshold
  Branch flow > some threshold
If condition is true in the result of primary contingency, implement a secondary contingency
Report violation only if some exists in the result of the
secondary contingency
Report if condition was true
NERLDC

## Slide 80: RTCA: Input and Output
CTGS
Contingency definitions
Input:
NETMOM
Contingency definitions
Output:
Basecase violations
Effect of contingencies:
  monitored element violations
  loss of load
  loss of generation
  islanding
BASECASE
PWRFLOW or RTNET
G G
STCA or RTCA
G
G
NERLDC

## Slide 81: CA : Specifying contingency screening parameters
 Violation
tolerances
 by type of monitored element
NERLDC

## Slide 82: RTCA : Ranking parameters
Contingencies are ranked in screening phase based on
The magnitude of violations they cause
The level of limit being violated ( 1 2 3 )
A ranking number is calculated for each type of
violation :
RANK = (level violated) * WT1 + (percent violation) * WT2
Weighting of violated level in contingency ranking
Weighting of violated percentage in contingency
WT1 :
WT2 :
ranking
NERLDC

## Slide 83: RTCA : Selection parameters
Selection uses the contingency severity rank:
User specifies the max number of potentially harmful contingencies to be retained for full analysis
Separately by constraint violation type : N1 N2 N3 N4
NERLDC

## Slide 84: CA : Defining Contingencies
Enter contingency ID
Press Define New Contingency button
Make outage selections
Save your selections
If desired, include
conditional monitored element definition
Enter contingency details
Validate your entries
Save contingency definition
NERLDC

## Slide 85: CA : Assigning contingencies to contingency groups
Individual contingencies can belong to more than one group
INSERT contingency group records
INSERT contingency records
Individual contingencies assigned to group
NERLDC

## Slide 86: CA : Activating contingencies by group
Click
to activate CTG group
NERLDC

## Slide 87: CA : Modifying contingency activation status
SET to MUSTRUN to
force activation
SET to INELIGIBLE to
prevent activation
NERLDC

## Slide 88: CA : Results Summary
NERLDC

## Slide 89: Load Forecasting
NERLDC

## Slide 90: LF : System Load Forecasting
Purpose
Provide system load forecast for each of the top level load areas in the load model hierarchy and their total
Short-term (horizon : 7 days ; time step : 1 or 1/2 hour)
Load forecast can be fed automatically to :
  The short-term operations planning tools : e- terracommit
  The bus loads forecasting function in the power flow application

## Slide 91: LF : System Load Forecasting
Features
Develops weather profiles to enable interpolation between entered weather forecasts
Uses forecasted values of weather variables entered manually or
retrieved from files
Can produce a forecast for several “forecast areas”
External area loads can be specified as a function of the internal forecast areas
LF can produce a forecast for areas without weather variable
Provides extensive data change capabilities :
  2 weeks in the past
  schedule of corrections to be applied in the future
  automatic re-scaling between 2 user specified points
Tracks forecasting error characteristics
NERLDC

## Slide 92: LF : Related applications
 Provides 2 different applications
LFMODEL application
  Model definition
  Off-line study
LF application
  On-line forecasting
NERLDC

## Slide 93: LF Model Preparation
Define/modify the model
Validate the model
Retrieve historical data
Remove abnormal days
Perform a study load forecast
Correct data errors
Evaluate the results
savecases
Historical data files
retrieve additional historical data
NERLDC

## Slide 94: Retrieve Historical Information
 Populating Historical Data
Historical load and weather profiles are received in MS Excel Format.
Data are exported to a text (.archive) file.
NERLDC

## Slide 95: On-lining the model
LFMODEL
LF
database
database
 LF database on-lining copies from LFMODEL to LF:
The model structure
All model parameters
All historical data
NERLDC

## Slide 96: Online Load Forecast Techniques
 Online Load Forecasting can be performed following 2 methods
Regression model :
  Using the short-term load forecast model
  Based on weather forecast
Non-Regression model :
  Using similar days facilities.
  Using load shapes facilities.
NERLDC

## Slide 97: LF : Similar Day Forecast
 ALTERNATE FORECAST based on SIMILAR-DAY
User can select to use similar-day forecast instead of automatic forecast
Similar-day forecast is built from historical loads as follows :
  for a particular load area and for a particular date, enter the search parameters :
    weather variables (up to 3) to compare with the weather forecast
    positive weight for each weather variable
    days-of-the-week to search
    months-of-the-year to search
  command execution of the search : days found are presented in decreasing order of the fit quality
  user selects the desired similar-day
There is no adjustment of the similar-day forecast to account for weather
differences
NERLDC

## Slide 98: Similar Day Forecasting
24
1
Temperature
Time in Hours
a
b
Weather forecast for a future day Weather for day x in the past Weather for day y in the past
Best fit
NERLDC

## Slide 99: LF : Load Shapes Library
 ALTERNATE FORECAST based on SHAPES
User can select to use alternate forecast instead of automatic forecast
Alternate forecast is built from a library of load shapes
Load shape library is created as follows :
  user selects the historical load curve
    for a particular load area
    for a particular date
  user assigns an ID and a name to that load shape (up to 32 curves)
Alternate load forecast is built as follows :
  for a particular load area and for a particular date
    user selects the desired load shape from the library
    user enters desired MIN and MAX loads [ MW ]
    selected load shape is re-scaled between 2 specified points
NERLDC

## Slide 100: Load Shape forecasting
Load History
Shapes Library
Day in forecast period
Scaling
NERLDC

## Slide 101: OPF, SENH, VVD
NERLDC

## Slide 102: OPF (optimal power flow)
 OPF scope: any problem that involves the determination of the optimal steady-state operation of an Electric Power Generation-Transmission system
 Optimal Power Flow (OPF) = Power Flow +
+ Objective
+ Controls
+ Constraints
 Objective : value to be minimized, such as cost or MW losses
 Controls : unit MW, unit MVAR, capacitors and reactors, ULTC and phase
shifter taps, and area interchanges
 Constraints : high and low voltage limits, branch flows, interface flow limits, and node pair limits
NERLDC

## Slide 103: Security Enhancement(SENH)
Can network security be improved?
Can operating costs be reduced?
MW MVAr
kV
TAP MW MVAr
MW MVAr
G
MW
G MVAr
Load
 Security Enhancement looks for control changes in order to improve
the security and the economics of the power system:
For the basecase network state (current or postulated)
 A feasible state is a network solution in which all components
operate within their limits
 An optimal state is a feasible state for which the operating cost has been reduced to a minimum
NERLDC

## Slide 104: Voltage – Var Dispatch (VVD)
 Purpose
Provide real-time recommendations regarding voltage related controls :
  voltage regulator set-points
  tap positions for non-regulating transformer
  connection status for non-regulating shunt reactance
In order to eliminate voltage violations and minimize transmission losses (if a feasible solution can be found)
 Features
OPF algorithm with fixed MW controls, applied to SE results
Flexible definition of controls
Flexible definition of constraints to be enforced
MVAr gen. limits given the current MW output
SVC (static VAr compensators)
  either as a fixed shunt reactance
  or as regulating a fixed voltage set-point
NERLDC

## Slide 105: QUESTIONS?
LIMITATIONS!
NERLDC

## Slide 106
You
Thank